BR.W511 Series

Self-operated control valve

INSTRUCTION

MANUAL

ZHEJIANG LASEN INTELLIGENT EQUIPMENT CO.,LTD

CATALOG

1.Product Overview and Features	2

2.Structure and Principle	2

2.1．Structure	2

2.2. Operation principle	3

2.3. Actuator Part	3

3.Installation and Maintenance	4

3.1. Installation	4

3.2. Installation mode	4

3.3. Adjustment	7

3.4. Use	7

3.5. Maintenance	7

4.Instructions for ordering	8

5.Appendix	9

Appendix I: Main technical parameters	9

Appendix II: Material of main parts	10

Appendix III. Size and weight of self operated control valve	10

- 1.Product Overview and Features

BR.W511 Series direct acting self operated control valve is a kind of pressure regulating valve which uses the pressure change of controlled medium itself to promote the actuator without external energy, so as to achieve the function of automatic regulation and pressure stabilization. It can work without electricity or gas.

The pressure regulating valve is mainly used for the pressure reduction and stabilization of steam, as well as the pressure stabilizing device for various gases and low viscosity liquid media.

Pressure regulating valve is widely used in chemical industry, petroleum, metallurgy, electric power, textile and other industrial sectors.

- 2.Structure and Principle

- 2.1．Structure

The pressure regulating valve is composed of actuator, regulating valve, pressure pipe, etc., as shown in Figure 1(a)(b)。

Fig 1(a) BR.W511 series outlet valve pressure control type           Fig 1(b) BR.W511 series inlet pressure control type

1.Body  2.Seat  3.Plug  4.Gasket  5.Bonnet  6.Bellows  7.Pressure regulating plate  8.Packing  9.Packing sleeve 10.Packing plate  11.Spring pad  12.Diaphragm cap 13.Diaphragm  14.Diaphragm cap  15.Supporting plate 16.Needle bearing  17.Stem  18.Outer ring spring 19.Inner ring spring 20.Column 21.Condenser 22.Pressure tap 23.Globe valve 24.Pressure tap

- 2.2. Operation principle

Fig 1(a): It is used for the pressure control of outlet. The initial position of the valve is at the opening position of the plug. The medium enters the valve body from the arrow direction and is throttled by the plug and valve seat. The medium behind the valve is introduced into the actuator through the connecting pipe. If the pressure behind the valve increases, the force acting on the diaphragm of the actuator will increase, and the spring will be compressed to drive the spool to reduce the opening of the valve until the pressure behind the valve drops to the set value. Similarly, if the pressure behind the valve is lower than the set value of pressure, the force acting on the diaphragm of the actuator will decrease. Under the action of spring force, the spring will drive the plug to increase the opening degree of the valve until the pressure behind the valve rises to the set value.

Fig 1(b): It is used for pressure control of inlet. The initial position of the valve is at the closing position of the plug, and the medium enters the valve body from the arrow direction. At the same time, the actuator is introduced through the front connecting pipe. If the pressure in front of the valve increases, the force acting on the diaphragm of the actuator will increase, and the spring will drive the plug to increase the opening degree of the valve until the pressure in front of the valve drops to the set value. Similarly, if the pressure in front of the valve decreases, the force acting on the diaphragm of the actuator decreases. Under the action of spring force, the spring drives the plug to reduce the valve opening until the pressure in front of the valve rises to the set value.

- 2.3. Actuator Part

Sheet1  Main technical parameters of actuator

| Model Spec | Diaphragm | Piston | Bellow |
| --- | --- | --- | --- |
| Purpose | Regulating |  |  |
| material | NBR, fluororubber, oil resistant rubber | aluminium alloy | 304、316 |
| Connection | M16×1.5 |  |  |
| Action Mode | The pressure rise valve opens , the pressure rise valve closes |  |  |
| Medium Temperature | Gas :-20～+80℃, Liquid:-20～+140℃, With condenser and heat sink: -20～+350℃ |  | -60～+250℃ |

- 3.Installation and Maintenance

- 3.1. Installation

Before installation, check whether the product model and specification meet the requirements, and the pipeline shall be cleaned to remove welding slag and sundries.

Select the correct installation mode according to table 4.

During installation, the pressure measuring point shall be at the proper position of the pressure regulating valve. The distance between the pressure opening type (K type) pressure regulating valve and the front flange of the valve shall be greater than 2 times of the pipe diameter; the distance between the pressure closing type (type b) pressure regulating valve and the back flange of the valve shall be greater than 6 times of the pipe diameter.

When the medium is steam, the pressure regulating valve must be inverted, and the condenser must be equipped. The condenser should be higher than the actuator membrane chamber and lower than the process pipeline to ensure that the membrane chamber and condenser are full of condensate.

In order to facilitate maintenance, the pressure regulating valve should be equipped with a bypass system.

- 3.2. Installation mode

P1 Regulating gas, outlet pressure regulating type (it is not necessary to install the filter)

P2 Regulating gas, inlet pressure regulating type (it is not necessary to install the filter)

P3 Regulating liquid, outlet pressure regulating type(for non clean liquid, it is recommended to install filter)

P4 Regulating liquid, inlet pressure regulating type(for non clean liquid, it is recommended to install filter)

P5 Regulating steam, outlet pressure regulating type(Condenser should be installed, filter is recommended)

P6 Regulating steam, inlet pressure regulating type(Condenser should be installed, filter is recommended)

Note

1：When installing condenser, pay attention to the condenser position, so that it is higher than the actuator and lower than the process pipe, so as to ensure that the condenser is filled with condensate;

2：Before using the condenser, open the plug of water injection port and inject pure water or condensate water (it must be filled up).

- 3.3. Adjustment

The required pressure value is adjusted through the operation of the pressure regulating plate (see Fig. 1). Clockwise rotation increases the pressure, while counter clockwise rotation decreases the pressure. Pay attention to the indication value of the pressure gauge. Until the indicated value of the pressure gauge meets the process requirements.

- 3.4. Use

(1)When the controlled medium is gas or low viscosity liquid.

Slowly open the stop valve, loosen the exhaust plug until the gas (or liquid) overflows from the exhaust hole of the actuator, then tighten the exhaust plug, and then adjust the pressure regulating plate until the pressure meets the requirements.

(2)When the controlled medium is steam

Screw out the liquid injection port screw from the condenser, loosen the exhaust plug of the actuator, use a funnel to add water through the liquid injection port until the water overflows from the liquid injection port, tighten the exhaust plug and liquid injection port screw, slowly open the stop valve, and adjust the pressure regulating plate until the pressure meets the requirements.

- 3.5. Maintenance

After the pressure regulating valve is put into operation, the general maintenance work is very small, usually only need to observe the pressure before and after the valve. See sheet 2 for common faults and troubleshooting of pressure regulating valve.

Sheet 2 common faults and troubleshooting

| Fault | Cause | troubleshooting |
| --- | --- | --- |
| The pressure of outlet is unstable and changes with the pressure in front of the valve | 1.The plug is stuck by foreign matters 2.The valve rod and push rod are stuck 3.The liquid inlet pipe is blocked | 1.Reassemble and remove foreign matters 2.Readjustment 3.Dredge the liquid inlet pipe |
| The pressure of outlet can not be reduced, and it is always above the demand value | 1.The stiffness of the set spring is too large 2.The valve diameter is too large | 1.Replace the spring 2.Replace the valve |
| The pressure of outlet can not rise, and it is always below the demand value | 1.The set spring stiffness is too small 2.Valve diameter too small 3.The pressure difference before and after the valve is too small | 1.Replace the spring 2.Replace the valve 3.Increase the pressure in front of the valve |
| The pressure of inlet can not rise, and always acts under the evaluation | 1.The set spring stiffness is too small 2.The plug is stuck by foreign matters 3.The plug and seat are damaged and the leakage is too large 4.The valve diameter is too large | 1.Replace the spring 2.Reassemble 3.Regrind or replace 4.Replace the valve |
| The pressure of inlet does not drop, and it always acts above the value to be evaluated | 1.Setting the spring stiffness too high 2.The valve diameter is too small 3.Plug, valve stem, push rod, etc. are stuck | 1.Replace the spring 2.Replace the valve 3.Reassemble |

- 4.Instructions for ordering

- Product model and name

- Nominal pressure

- Nominal diameter

- Pressure before and after the valve

- Mediumn, density and temperature

- Medium’s maximum, normal and minimum flow

- Inherent flow characteristics of valve

- Overall action mode, gas source pressure, signal range

- Valve body and trim material

- Explosion proof requirements

- Accessories and other special requirements

- 5.Appendix

- Appendix I: Main technical parameters

Sheet 3-1  BR.W511 series standard type

| Nominal diameter |  | 20 | 25 | 32 | 40 | 50 | 65 | 80 | 100 | 125 | 150 | 200 | 250 | 300 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rated Kv | Single seat | 7 | 11 | 20 | 30 | 48 | 75 | 120 | 190 | 300 | 480 | 760 | 1100 | 1750 |
|  | Sleeve | 7 | 11 | 20 | 30 | 48 | 75 | 120 | 190 | 300 | 480 | 760 | 1100 | 1750 |
|  | Double seat | - | - | 22 | 33 | 53 | 83 | 132 | 209 | 330 | 528 | 836 | 1210 | 1925 |
| Rated stroke L(mm) |  | 8 |  | 10 |  | 12 | 20 |  | 22 |  | 25 | 25 | 25 | 25 |
| Inherent flow characteristics |  | Quick open, Fixed linear |  |  |  |  |  |  |  |  |  |  |  |  |
| Pressure regulation range (KPa) |  | 15-50 40-80 60-100 80-140 120-180 160-220 200-260 240-300 280-350 330-400 380-450 430-500 480-560 540-620 600-700 680-800 780-900 880-1000 950-1500 1000-2500 2000-3000 2500-3500 |  |  |  |  |  |  |  |  |  |  |  |  |
| Adjustment accuracy |  | ±8% |  |  |  |  |  |  |  |  |  |  |  |  |
| Allowable leakage |  | Metal seal: Ⅳ(10−4×Kv);Soft seal:Ⅵ(ACC GB/T4213-2008) |  |  |  |  |  |  |  |  |  |  |  |  |

- Note: pressure regulation range can be customized according to customer’s requirements

Sheet 3-2  BR.W511 Series low flow type

| Nominal diameter | 20、25 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 12 | 15 |
| Rated Kv | 0.02 | 0.08 | 0.12 | 0.20 | 0.32 | 0.5 | 0.8 | 1.2 | 1.8 | 2.5 | 4 |
| Rated stroke L(mm) | 5 |  |  |  |  |  |  |  |  |  |  |
| Inherent flow characteristics | Linear, Fixed linear |  |  |  |  |  |  |  | Quick open |  |  |
| Adjustment accuracy | ±8% |  |  |  |  |  |  |  |  |  |  |
| Allowable leakage | Metal seal: Ⅳ(10−4×Kv);Soft seal:Ⅵ(ACC GB/T4213-2008) |  |  |  |  |  |  |  |  |  |  |

- Note: pressure regulation range can be customized according to customer requirements

- Appendix II: Material of main parts

Sheet 4

| Part name | Material |
| --- | --- |
| Body, bonnet | WCB WC6 LCB CF8 CF8M CF3 CF3M |
| Trim | 0Cr18Ni9(304);0Cr17Ni12Mo2(316) 00Cr17Ni14Mo2(316L) Above+R.TFE(Modified PTFE) Above+Stellite(Hardfacing stellite alloy) |
| Packing | V-type PTFE, Modified PTFE, Flexible graphite |
| Spring | 60Si2Mn |
| Diaphragm cap | Q235, SS |
| bushing、guiding sleeve type | 2Cr13、0Cr18Ni9、1Cr18Ni9Ti、QAL9-4 |

- Appendix III. Size and weight of self operated control valve

- BR.W511 Series outlet control type(Diaphragm Actuator)

Sheet 5-1 Size of outlet control type  Unit: mm

| DN | L |  | H | H1 | A | L1 | P | Weight(Kg) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | PN16,40 | PN63,100 |  |  |  |  |  | PN16 | PN63 |
| 20 | 150 | 206 | 470 | 42 | ¢176 ¢196 ¢232 ¢282 ¢308 | 250 | 180 | 26 | 31 |
| 25 | 160 | 210 | 475 | 48 |  | 250 | 180 | 26 | 31 |
| 32 | 180 | 220 | 510 | 56 |  | 300 | 220 | 36 | 43 |
| 40 | 200 | 251 | 520 | 64 |  | 300 | 220 | 37 | 44 |
| 50 | 230 | 286 | 530 | 76 |  | 370 | 300 | 42 | 50 |
| 65 | 290 | 311 | 550 | 85 |  | 520 | 400 | 73 | 88 |
| 80 | 310 | 337 | 680 | 100 |  | 520 | 400 | 90 | 108 |
| 100 | 350 | 394 | 750 | 110 |  | 670 | 570 | 115 | 138 |
| 125 | 400 | 460 | 800 | 126 |  | 980 | 900 | 130 | 156 |
| 150 | 480 | 508 | 870 | 160 |  | 980 | 900 | 145 | 174 |
| 200 | 600 | 610 | 890 | 202 |  | 1200 | 1050 | 180 | 216 |
| 250 | 730 | 752 | 910 | 270 |  | 1500 | 1250 | 200 | 240 |
| 300 | 850 | 819 | 950 | 290 |  | 1500 | 1350 | 250 | 300 |

- Note：1. The size in the table is PN16 standard configuration data, if you need different pressure level parameters, please contact our company.

- Our company can customize and produce valve products under various harsh working conditions according to customers' requirements. If customers have no special requirements, we will supply according to standard configuration.

- 3. Stop valve and pressure connection pipe are non-standard valve accessories, which can be selected according to customer requirements.

- 4. L1 and P in the sheet are the standard configuration of our company. Generally, P ≥ 6 × DN can also be configured according to customer requirements.

BR.W511 Series inlet control type(Diaphragm Actuator)

Sheet 5-2 inlet control type  Unit: mm

| DN | L |  | H | H1 | A | L1 | P | Weight(Kg) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | PN16,40 | PN63,100 |  |  |  |  |  | PN16 | PN63 |
| 20 | 150 | 206 | 470 | 83 | ¢176 ¢196 ¢232 ¢282 ¢308 | 250 | 180 | 26 | 31 |
| 25 | 160 | 210 | 475 | 83 |  | 250 | 180 | 26 | 31 |
| 32 | 180 | 220 | 510 | 93 |  | 300 | 220 | 36 | 43 |
| 40 | 200 | 251 | 520 | 95 |  | 300 | 220 | 37 | 44 |
| 50 | 230 | 286 | 530 | 110 |  | 370 | 300 | 42 | 50 |
| 65 | 290 | 311 | 550 | 128 |  | 520 | 400 | 73 | 88 |
| 80 | 310 | 337 | 680 | 140 |  | 520 | 400 | 90 | 108 |
| 100 | 350 | 394 | 750 | 160 |  | 670 | 570 | 115 | 138 |
| 125 | 400 | 460 | 800 | 215 |  | 980 | 900 | 130 | 156 |
| 150 | 480 | 508 | 870 | 230 |  | 980 | 900 | 145 | 174 |
| 200 | 600 | 610 | 890 | 268 |  | 1200 | 1050 | 180 | 216 |
| 250 | 730 | 752 | 910 | 385 |  | 1500 | 1250 | 200 | 240 |
| 300 | 850 | 819 | 950 | 420 |  | 1500 | 1350 | 250 | 300 |

- Note：1. The size in the table is PN16 standard configuration data, if you need different pressure level parameters, please contact our company.

- Our company can customize and produce valve products under various harsh working conditions according to customers' requirements. If customers have no special requirements, we will supply according to standard configuration.

- Stop valve and pressure connection pipe are non-standard valve accessories, which can be selected according to customer requirements.

- L1 and P in the sheet are the standard configuration of our company. Generally, P ≥ 6 × DN can also be configured according to customer requirements.

ZHEJIANG LASEN INTELLIGENT EQUIPMENT CO.,LTD ADD:No. 15 Mashan Road, Changkou Industrial Zone, Fuyang District, Hangzhou, Zhejiang Province TEL:0571-23252111/23291601 FAX:0571-23291602 WEB:www.lasen.com.cn POST CODE:311401